## Slide 1
1
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Department of Plant and Environmental Sciences
1
Wastewater treatment in cold/arctic climate with a focus on small scale and onsite systems
Professor, Petter D. Jenssen
Department of Plant- and Environmental Sciences
Norwegian University of Life Sciences (UMB)
28th Alaska Health Summit, January 10-13, 2011

## Slide 2
January 11, 11
2
Extremely cold climate

## Slide 3: Large areas - extremely low population density
January 11, 11
The world’s biggest island
The ice free area 19%
Inhabitants 50.000
Climate differs from one locality to the other

## Slide 4
January 11, 11
Sisimiut Greenland, 5000 people (2500 dogs)

## Slide 5
January 11, 11
5
Low income - poor communities

## Slide 6
January 11, 11
6
Social stress

## Slide 7
January 11, 11
7
Water pipe

## Slide 8: Wastewater handling in Greenland
January 11, 11
Wastewater is led untreated to the recipients everywhere in Greenland
  This goes for both black wastewater (toilet waste) and gray wastewater (wastewater from kitchen, bathroom and washing facilities)
30% of the Greenlandic residences were not connected to sewerage in 2001
Wastewater handling in Greenland - Towns
Wastewater pipes

## Slide 9
January 11, 11
9
Sewer outlet

## Slide 10
January 11, 11
Wastewater handling in Greenland - towns and smaller settlements
”Honey
buckets”

## Slide 11
January 11, 11
”Honey
buckets”
Smell !
Dignity !
Health risk !
Wastewater handling in Greenland - towns and smaller settlements

## Slide 12
Sewage outlet

## Slide 13
January 11, 11
10

## Slide 15
January 11, 11
13
Greywater outlet

## Slide 16
January 11, 11
12
Frozen greywater

## Slide 17
January 11, 11
Department of Plant and Environmental Sciences
14

## Slide 18
January 11, 11
15
Greywater discharge pipe

## Slide 19: Handling of wastewater in the Arctic
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
19
Sewage outlet
Wastewater is led untreated to the recipients everywhere in Greenland
WHY IS WASTEWATER HANDLING POORLY DEVELOPED
WHAT ARE THE CONSEQUENCES FOR THE WATER ENVIRONMENT?
Department of Plant and Environmental Sciences

## Slide 20: Wastewater transport in the arctic is challenging Piping systems
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
20
20
Photos: Frøydis M. Reinhart
Department of Plant and Environmental Sciences

## Slide 21: Wastewater handling in Greenland
January 11, 11
Wastewater is led untreated to the recipients everywhere in Greenland
  This goes for both black wastewater (toilet waste) and gray wastewater (wastewater from kitchen, bathroom and washing facilities)
30% of the Greenlandic residences were not connected to sewerage in 2001
Wastewater handling in Greenland
Wastewater pipes

## Slide 22
January 11, 11
Piping systems are extremely expensive
Wastewater handling in the Arctic

## Slide 23
January 11, 11
Piping systems are extremely expensive
Treatment processes are challenging/expensive to operate
Wastewater handling in the Arctic

## Slide 24: Handling of wastewater in the Arctic
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
24
Sewage outlet
Wastewater is led untreated to the recipients everywhere in Greenland
WHY IS WASTEWATER HANDLING POORLY DEVELOPED?
WHAT ARE THE CONSEQUENCES FOR THE WATER ENVIRONMENT AND HEALTH?
Department of Plant and Environmental Sciences

## Slide 25
Wastewater discharge to arctic waters – problems?
Nutrients (nitrogen and phosphorus) ?
Organic matter ?
Pathogens, microorganisms ?

## Slide 26
Wastewater discharge to arctic waters – problems?
Nutrients (nitrogen and phosphorus) ?
Organic matter ?
Pathogens, microorganisms ?
50 000
inhabitants

## Slide 27
Wastewater discharge to arctic waters – problems?
Nutrients (nitrogen and phosphorus) ?
Organic matter ?
Pathogens, microorganisms?
Ulkebugten

## Slide 28
Wastewater discharge to arctic waters – problems?
Nutrients (nitrogen and phosphorus) ?
Organic matter a local problem
Pathogens, microorganisms?
Ulkebugten

## Slide 29
Wastewater discharge to arctic waters – problems?
Nutrients ?
Organic matter ?
Pathogens ?
Organic micropollutants ?
* Medicine residues
* POP´s
Sisimiut Greenland
Hospital
Sewage outlet

## Slide 30
Wastewater discharge to arctic waters – problems?
Nutrients ?
Organic matter ?
Pathogens ?
Organic micropollutants ?
* Medicine residues
* POP´s
Sisimiut Greenland
Antibiotic resistant bacteria
Higher concentration of antibiotic resistant bacteria close to the outlet from the hospital (Project Maribact)

## Slide 31
Wastewater discharge to arctic waters – problems?
Nutrients ?
Organic matter ?
Pathogens ?
Organic micropollutants ?
* Medicine residues
* POP´s
Sisimiut Greenland
Antibiotic resistant bacteria
Higher concentration of antibiotic resistant bacteria close to the outlet from the hospital (Project Maribact)
Pharmaceutical residues
It has been shown that hormones for instance affect fish at remarkably low concentration (1,0 ng/L) (Routledge et al., 1998, Purdom et al., 1994)

## Slide 32
Accumulation of unwanted substances in the food chain

## Slide 33
Wastewater discharge to arctic waters – problems?
Nutrients - no problem
Organic matter a local problem
Antibiotic resistant bacteria
Organic micropollutants
* Medicine residues
* POP´s

## Slide 34: Solutions to the sanitary challenges
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Centralized systems
Onsite systems (decentralized)
Systems with source separation (decentralized)
  Low flush, dry or incineration toilets
  Urine divertion
  Greywater treatment
34
Department of Plant and Environmental Sciences

## Slide 35: Solutions to the sanitary challenges
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Centralized systems
Onsite systems (decentralized)
Systems with source separation (decentralized)
  Low flush, dry or incineration toilets
  Urine divertion
  Greywater treatment
35
Department of Plant and Environmental Sciences

## Slide 36
January 11, 11
Piping systems are extremely expensive
Treatment processes are challenging/expensive to operate
Wastewater handling in the Arctic

## Slide 37
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
37
Cost aspects of of centralized sewer systems
Collection system 70 - 90 %
Treatment 10 - 30 %
(Otis 1996, Mork et al. 2000)
Department of Plant and Environmental Sciences

## Slide 38
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
38
Cost aspects of of centralized sewer systems
Collection system 70 - 90 %
Treatment 10 - 30 %
(Otis 1996, Mork et al. 2000)
ENERGY:
The water sector is the forth most energy intensive sector in the UK
(The Parliamentary Office of Science and Technology, 2007)
Department of Plant and Environmental Sciences

## Slide 39
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
39
Centralized vs. decentralized
Centralized systems are expensive both to construct and to operate. If adequate decentralized systems (from a technical, economical and social aspect) are available these should be preferred
Department of Plant and Environmental Sciences
Photo: F. Reinhardt

## Slide 40: Solutions to the sanitary challenges
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Centralized systems
Onsite systems (decentralized)
Systems with source separation (decentralized)
  Low flush, dry or incineration toilets
  Urine divertion
  Greywater treatment
40
Department of Plant and Environmental Sciences

## Slide 41
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
41
Onsite systems - technology options
Department of Plant and Environmental Sciences

## Slide 42
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
42
Onsite systems
Department of Plant and Environmental Sciences

## Slide 43: Drip irrigation
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
43
Department of Plant and Environmental Sciences

## Slide 44: Drip irrigation
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
44
Department of Plant and Environmental Sciences
Treatment performance Overall | High
Treatment performance Hygiene | High
Investment cost | Medium/high
O&M | Medium
Technical complexity | Low/medium
Suitability arctic conditions | Low/medium

## Slide 45
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
45
Onsite systems
Department of Plant and Environmental Sciences

## Slide 46
46
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Soil infiltration systems - system types
Open systems - infiltration in ponds
Subsurface (buried) systems - infiltration trenches

## Slide 47
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Department of Plant and Environmental Sciences
47
Groundwater level
Treatment results rapid infiltration Norway
COD Phosphorus Nitrogen (Kraft 1998)
Fecal coli.
<100/100ml

## Slide 48: Buried soil infiltration systems - design types
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
48
Source: www.avlop.no
DEPARTMENT OF PLANT AND ENVIRONMENTAL SCIENCES
Mound
Surface infiltration
Shallow infiltration
Deep
infiltration
Septic tank
Pump/dosing
device
Soil
Bedrock

## Slide 49
49
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Soil infiltration systems
Open systems - infiltration in ponds
Subsurface (buried) systems - infiltration trenches
Treatment performance Overall | High
Treatment performance Hygiene | High
Investment cost | Low
O&M | Low
Technical complexity | Low/medium
Suitability arctic conditions | Low/medium
Department of Plant and Environmental Sciences

## Slide 50
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
50
Onsite systems
Department of Plant and Environmental Sciences

## Slide 51
51
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
DEPARTMENT OF PLANT AND ENVIRONMENTAL SCIENCES
7
Domestic WW: 7 - 9 m3/person
Greywater: 2- 3 m3/person
40 m2/family
Constructed wetlands / filterbeds

## Slide 52: Constructed wetland/Filterbed
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
52
Department of Plant and Environmental Sciences
Septic
tank
Pump
Biofilter
Subsurface flow
filterbed

## Slide 53
53
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Compact filterbed
Department of Plant and Environmental Sciences
Septic tank
Biofilter
Upflow filter
Notes: Anleggskomponentene. Etter dette kommer en animasjon

## Slide 54
54
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Spiking with virus
Inlet concentration
Biofilter effluent conc.
Final effluent conc.
3 - 4 log10 virus and E.coli reduction
COMPACT FILTER
Department of Plant and Environmental Sciences
Notes: Anleggskomponentene. Etter dette kommer en animasjon

## Slide 55: Constructed wetland/Filterbed - verdict
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
55
Treatment performance Overall | High
Treatment performance Hygiene | High
Investment cost | High /medium
O&M | Medium
Technical complexity | Medium
Suitability arctic conditions | Medium/high
Department of Plant and Environmental Sciences

## Slide 56
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
56
Onsite systems
Department of Plant and Environmental Sciences

## Slide 57: Sewage lagoons/ponds
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
57
Iqaluit’s Sewage Lagoon
Baffin Island
Department of Plant and Environmental Sciences

## Slide 58: Sewage lagoons - pond systems
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
58
Photo: F. Reinhardt
Baffin Island
Treatment performance Overall | Low/medium
Treatment performance Hygiene | Low/medium
Investment cost | Low/medium
O&M | Low/medium
Technical complexity | Low/medium
Suitability arctic conditions | Low/medium
Department of Plant and Environmental Sciences

## Slide 59
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
59
Onsite systems
Department of Plant and Environmental Sciences

## Slide 60: Package treatment plants - downsized conventional systems
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
60
Different designs
Department of Plant and Environmental Sciences

## Slide 61: Package treatment plant - Sisimiut
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
61
Department of Plant and Environmental Sciences

## Slide 62: Package treatment plant - Sisimiut
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
62
Department of Plant and Environmental Sciences

## Slide 63
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
63
Department of Plant and Environmental Sciences

## Slide 64: Package treatment plant - Sisimiut
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
64
Department of Plant and Environmental Sciences

## Slide 65: Package treatment systems
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
65
Treatment performance Overall | Medium
Treatment performance Hygiene | Low/medium
Investment cost | High /medium
O&M | High
Technical complexity | High
Suitability arctic conditions | Low
Department of Plant and Environmental Sciences

## Slide 66: Solutions to the sanitary challenges
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Centralized systems
Onsite systems (decentralized)
Systems with source separation (decentralized)
  Low flush, dry or incineration toilets
  Urine divertion
  Greywater treatment
66
Department of Plant and Environmental Sciences

## Slide 67
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Department of Plant and Environmental Sciences
67
(Alsen and Jenssen2005)
Source separation of wastewater

## Slide 68
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
68
Data from: Cordell et al. 2009
Department of Plant and Environmental Sciences

## Slide 69: Source separation - toilet options
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
69
0 Incinerating toilets
Department of Plant and Environmental Sciences

## Slide 70: Source separation - toilet options
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
70
0 Incinerating toilets
Department of Plant and Environmental Sciences

## Slide 71: Contribution from the toilet * 90 % of N * 80 % of P * 80 % of K * 40-75 % of org. matter * Majority of the pathogens
71
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Department of Plant and Environmental Sciences
Notes: The majority of the nutrients in wastewater originates from our excreta, urine and feces and ends up in the toilet waste termed blackwater;

## Slide 72: Contribution from the toilet 6 - 20 liters per flush ! 20 - 40% of the total water use !
72
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Department of Plant and Environmental Sciences
Notes: The majority of the nutrients in wastewater originates from our excreta, urine and feces and ends up in the toilet waste termed blackwater;

## Slide 73: Future toilet types (commercially available today)
73
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
    Composting /dry sanitation 0 - 0.1 liter/visit
    Urine diverting 0.1 - 4.0 liter/visit
    Water saving (vacuum&gravity) 0.5 - 1.0 liter/visit
    Incinerating 0 liter/visit
Water use
Department of Plant and Environmental Sciences

## Slide 74: Future toilet types (commercially available today)
74
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
    Composting /dry sanitation 0 - 0.1 liter/visit
    Urine diverting 0.1 - 4.0 liter/visit
    Water saving (vacuum&gravity) 0.5 - 1.0 liter/visit
    Incinerating 0 liter/visit
Water use
Department of Plant and Environmental Sciences

## Slide 75
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
75
Incinerating toilets

## Slide 76: Incinerating toilets
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
76
1
2
3
Department of Plant and Environmental Sciences

## Slide 77
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
77
Troll - the Norwegian research station in Antartica

## Slide 78
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
78
Incinerating toilets
User friendliness | Medium/low
Hygiene | High
Investment cost | High
O&M | High
Technical complexity | High
Suitability arctic conditions | Low/medium
Department of Plant and Environmental Sciences

## Slide 79: Future toilet types (commercially available today)
79
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
    Composting /dry sanitation 0 - 0.1 liter/visit
    Urine diverting 0.1 - 4.0 liter/visit
    Water saving (vacuum&gravity) 0.5 - 1.0 liter/visit
    Incinerating 0 liter/visit
Water use
Department of Plant and Environmental Sciences

## Slide 80: Composting toilet at roadside facility - Sweden
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
80
Elected the best
roadside facility
in Sweden 2003 - 2008
Department of Plant and Environmental Sciences

## Slide 81: Composting toilet system - removable compartments
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
81
Department of Plant and Environmental Sciences

## Slide 82: Composting toilet at roadside facility - Sweden
82
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Clean odourless
toilets
Department of Plant and Environmental Sciences

## Slide 83: Composting toilet - bathroom design
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
83
High standard and comfort possible
Department of Plant and Environmental Sciences

## Slide 84: Composting toilets - design
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
84
Department of Plant and Environmental Sciences
Single
compartment
Dual
compartments
Removable
compartments

## Slide 85
85
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Composting toilets - advantages
Department of Plant and Environmental Sciences
Volume reduction:
70 - 90%
550 down to 55 liters
Uses no water
Simple and robust
(Del Porto and Steinfeld 1999)

## Slide 86
86
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
Composting toilet - challenges
Public acceptance
Maintenance
Excess liquid
Insulation
Hygiene
- no system
above 43oC
- risk of handling
Department of Plant and Environmental Sciences

## Slide 87
Secondary composting
Temperature:
Outside -54C
Inside +12C
Final product

## Slide 88
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
88
International research show that dry sanitation may give an equal or higher reduction of pathogens and a high reduction in risk of exposure.
(Stenström 2001)
Composting toilets – an option for the Arctic ?
Department of Plant and Environmental Sciences

## Slide 89: Conclusions
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
89
Secondary composting opens for professional collection and treatment of material from composting toilets- thus reducing health risk
Department of Plant and Environmental Sciences
Composting toilet - handling

## Slide 90: Conclusions
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
90
Department of Plant and Environmental Sciences
Composting toilet - handling
User friendliness | Medium/high
Hygiene | High
Investment cost | High/low
O&M | Medium/low
Technical complexity | Low
Suitability arctic conditions | High*

## Slide 91: Future toilet types (commercially available today)
91
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
    Composting /dry sanitation 0 - 0.1 liter/visit
    Urine diverting 0.1 - 4.0 liter/visit
    Water saving (vacuum&gravity) 0.5 - 1.0 liter/visit
    Incinerating 0 liter/visit
Water use
Department of Plant and Environmental Sciences

## Slide 92
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
92
Vacuum
0.5 - 1.5 liters/flush
Gravity
1 liter/flush
Department of Plant and Environmental Sciences
Low flush toilets – an option for the Arctic ?

## Slide 93
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
93
Contemporary Scandinavian bathroom design
using vacuum toilets
Photos: P.D. Jenssen
Low flush toilets – an option for the Arctic ?
Department of Plant and Environmental Sciences

## Slide 94
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
94
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank

## Slide 95
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
95
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Low flush
gravity toilet
Insulated
underground
holding tank
with heating
cable
Quick coupling
for easy
pumping

## Slide 96
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
96
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Low flush
gravity toilet
Quick coupling
for easy
pumping
?

## Slide 97
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
97
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Low flush
gravity toilet
Quick coupling
for easy
pumping

## Slide 98
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
98
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Blackwater
dewatering
unit
Quick coupling
for easy
pumping

## Slide 99
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
99
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic?
Blackwater dewatering unit

## Slide 100
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
100
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic?
Blackwater dewatering unit
Final products:
* Organic soil/compost
* Clear odorless liquid

## Slide 101
January 11, 11
”Honey
buckets”
Sisimiut Greenland
Modern
low flush
toilet

## Slide 102
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
102
Sisimiut Greenland

## Slide 103
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
103
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Blackwater
dewatering
unit
Quick coupling
for easy
pumping
Biogas digester

## Slide 104
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
104
Department of Plant and Environmental Sciences
Low flush toilets – adaption to the Arctic
Liquid level warning light
Insulated holding tank
Blackwater
dewatering
unit
Quick coupling
for easy
pumping
Biogas digester

## Slide 105
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
105
Sisimiut Greenland

## Slide 106: Kildesep prinsipp
January 11, 11
Thermophilic anaerobic
treatment - BIOGAS
Sisimiut – New possibilities
Waste incinerator
Growth medium
Nutrients
Energy

## Slide 107: Source separation - greywater
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
107
0 Incinerating toilets
Department of Plant and Environmental Sciences

## Slide 108
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
108
Onsite systems suitable for GREYWATER treatment
Department of Plant and Environmental Sciences

## Slide 109: Compact greywater treatment system
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
109
Department of Plant and Environmental Sciences
Producing efluent that
meets European bathing
water standards
(Ecomotive Inc.)

## Slide 110
January 11, 11
15
Greywater discharge pipe

## Slide 111
January 11, 11
Department of Plant and Environmental Sciences
14

## Slide 112
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
112
Department of Plant and Environmental Sciences
SANBOX – a solar powered treatment system for
remote locations such as mountain lodges

## Slide 113
Use greenhouse technology to provide processes energy from solar heat
Evaporate blackwater liquid fraction
Washing
facilities
treat
greywater
to swimming
water quality
Vacuum
toilet system
Dewater
and decompose
blackwater
solid fraction
high systems
reliability
with redundant
core
components
Recycling
nutrients
into products
such as
compost or
firewood
dizzy
toilet
The vision SANBOX

## Slide 114: Main conclusions
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
114
Organic micropollutants, including medicine recidues, and hygiene components may pose the highest environmental and health risk of wastewater discharge to arctic waters
Conventional centralized sewer systems are expensive to construct an operate and probably not sustainable.
There are options that can be used immediately or after some R&D
Decentralized/onsite systems and source separating systems especially have potential to solve the sanitation problems in a sustainable way
Department of Plant and Environmental Sciences

## Slide 115
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
115
Thank you !

## Slide 117
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
117
Nutrients and volume of domestic wastewater fractions
(Jönsson et al., 2000).
Department of Plant and Environmental Sciences

## Slide 118
NORWEGIAN UNIVERSITY OF LIFE SCIENCES
www.umb.no
118